Transmission Line Fault Detection: Model Comparison

Dataset: classdetectfault_data.csv, shape (7861, 11), 0 rows removed. Features: Ia, Ib, Ic, Va, Vb, Vc. Targets: G, C, B, A (fault type indicators). Train/test split: 6288 / 1573 samples (LSTM used event-based split: 2443 / 611 events).

Class Distribution

| Target | Class 0 | Class 0 % | Class 1 | Class 1 % |
| --- | --- | --- | --- | --- |
| G | 4465 | 56.80% | 3396 | 43.20% |
| C | 4628 | 58.87% | 3233 | 41.13% |
| B | 3494 | 44.45% | 4367 | 55.55% |
| A | 3369 | 42.86% | 4492 | 57.14% |

Per-Target Results by Model

G

| Model | Accuracy | Precision | Recall | F1 |
| --- | --- | --- | --- | --- |
| SVM (RBF) | 0.8856 | 0.8105 | 0.9653 | 0.8811 |
| Decision Tree | 0.8773 | 0.7964 | 0.9682 | 0.8739 |
| K-NN | 0.8970 | 0.8930 | 0.8698 | 0.8812 |
| CNN | 0.8824 | 0.7942 | 0.9884 | 0.8807 |
| LSTM | 0.8304 | 0.7265 | 0.9649 | 0.8289 |

C

| Model | Accuracy | Precision | Recall | F1 |
| --- | --- | --- | --- | --- |
| SVM (RBF) | 0.9930 | 0.9967 | 0.9853 | 0.9909 |
| Decision Tree | 0.9949 | 0.9967 | 0.9902 | 0.9934 |
| K-NN | 0.9975 | 0.9967 | 0.9967 | 0.9967 |
| CNN | 0.9968 | 0.9984 | 0.9935 | 0.9959 |
| LSTM | 0.9785 | 1.0000 | 0.9505 | 0.9746 |

B

| Model | Accuracy | Precision | Recall | F1 |
| --- | --- | --- | --- | --- |
| SVM (RBF) | 0.9917 | 0.9976 | 0.9870 | 0.9923 |
| Decision Tree | 0.9898 | 0.9976 | 0.9835 | 0.9905 |
| K-NN | 0.9962 | 0.9988 | 0.9941 | 0.9965 |
| CNN | 0.9968 | 1.0000 | 0.9941 | 0.9970 |
| LSTM | 0.9952 | 1.0000 | 0.9919 | 0.9960 |

A

| Model | Accuracy | Precision | Recall | F1 |
| --- | --- | --- | --- | --- |
| SVM (RBF) | 0.9981 | 0.9978 | 0.9989 | 0.9983 |
| Decision Tree | 0.9962 | 1.0000 | 0.9933 | 0.9966 |
| K-NN | 1.0000 | 1.0000 | 1.0000 | 1.0000 |
| CNN | 0.9994 | 1.0000 | 0.9989 | 0.9994 |
| LSTM | 0.9922 | 1.0000 | 0.9869 | 0.9934 |

Overall Model Summary

| Model | Mean Accuracy | Mean Precision | Mean F1 | Mean Latency (ms) | Mean Robustness | Overall Fault-Occurred Accuracy |
| --- | --- | --- | --- | --- | --- | --- |
| SVM (RBF) | 0.9671 | 0.9506 | 0.9657 | 1.4676 | 0.9661 | 0.9981 |
| Decision Tree | 0.9646 | 0.9477 | 0.9636 | 1.0060 | 0.9413 | 0.9981 |
| K-NN | 0.9727 | 0.9721 | 0.9686 | 20.4359 | 0.9540 | 1.0000 |
| CNN | 0.9688 | 0.9481 | 0.9683 | 83.9715 | 0.9685 | 0.9994 |
| LSTM | 0.9491 | 0.9316 | 0.9482 | 90.2303 | 0.9156 | 0.9994 |

Latency is measured per row/sample for SVM, Decision Tree, K-NN, and CNN (inference), and per sample (streaming) for LSTM. Robustness is the mean accuracy/F1 retained across the noise sweep (1%, 5%, 10%, 20%).

Robustness Sweep by Model, All Targets

Mean accuracy ± standard deviation across 10 trials per noise level. G is the hardest target across models and shows the widest spread; A and B are comparatively stable up to 10% noise for most models.

G

| Model | Noise 1% | Noise 5% | Noise 10% | Noise 20% |
| --- | --- | --- | --- | --- |
| SVM (RBF) | 0.8842 ± 0.0009 | 0.8785 ± 0.0028 | 0.8615 ± 0.0039 | 0.8187 ± 0.0053 |
| Decision Tree | 0.8467 ± 0.0028 | 0.7709 ± 0.0081 | 0.7070 ± 0.0120 | 0.6172 ± 0.0126 |
| K-NN | 0.8226 ± 0.0040 | 0.8530 ± 0.0047 | 0.8576 ± 0.0041 | 0.8446 ± 0.0049 |
| CNN | 0.8821 ± 0.0007 | 0.8752 ± 0.0032 | 0.8548 ± 0.0050 | 0.8036 ± 0.0065 |
| LSTM | 0.7663 ± 0.0012 | 0.7670 ± 0.0025 | 0.7671 ± 0.0041 | 0.7658 ± 0.0071 |

C

| Model | Noise 1% | Noise 5% | Noise 10% | Noise 20% |
| --- | --- | --- | --- | --- |
| SVM (RBF) | 0.9915 ± 0.0008 | 0.9797 ± 0.0029 | 0.9329 ± 0.0079 | 0.8631 ± 0.0066 |
| Decision Tree | 0.9837 ± 0.0020 | 0.8926 ± 0.0050 | 0.7833 ± 0.0075 | 0.6499 ± 0.0086 |
| K-NN | 0.9972 ± 0.0006 | 0.9894 ± 0.0019 | 0.9758 ± 0.0027 | 0.9449 ± 0.0047 |
| CNN | 0.9964 ± 0.0008 | 0.9723 ± 0.0032 | 0.9427 ± 0.0037 | 0.8861 ± 0.0058 |
| LSTM | 0.9788 ± 0.0003 | 0.9773 ± 0.0010 | 0.9650 ± 0.0025 | 0.9430 ± 0.0036 |

B

| Model | Noise 1% | Noise 5% | Noise 10% | Noise 20% |
| --- | --- | --- | --- | --- |
| SVM (RBF) | 0.9911 ± 0.0006 | 0.9835 ± 0.0028 | 0.9403 ± 0.0043 | 0.8617 ± 0.0088 |
| Decision Tree | 0.9707 ± 0.0024 | 0.8919 ± 0.0085 | 0.8053 ± 0.0059 | 0.6920 ± 0.0088 |
| K-NN | 0.9962 ± 0.0002 | 0.9925 ± 0.0011 | 0.9823 ± 0.0019 | 0.9561 ± 0.0028 |
| CNN | 0.9964 ± 0.0006 | 0.9723 ± 0.0026 | 0.9310 ± 0.0039 | 0.8576 ± 0.0029 |
| LSTM | 0.9698 ± 0.0009 | 0.9717 ± 0.0025 | 0.9703 ± 0.0033 | 0.9563 ± 0.0054 |

A

| Model | Noise 1% | Noise 5% | Noise 10% | Noise 20% |
| --- | --- | --- | --- | --- |
| SVM (RBF) | 0.9975 ± 0.0004 | 0.9909 ± 0.0008 | 0.9620 ± 0.0028 | 0.9031 ± 0.0090 |
| Decision Tree | 0.9640 ± 0.0030 | 0.8897 ± 0.0066 | 0.8316 ± 0.0086 | 0.7401 ± 0.0102 |
| K-NN | 0.9998 ± 0.0003 | 0.9970 ± 0.0008 | 0.9893 ± 0.0025 | 0.9671 ± 0.0039 |
| CNN | 0.9992 ± 0.0003 | 0.9857 ± 0.0041 | 0.9519 ± 0.0027 | 0.8957 ± 0.0044 |
| LSTM | 0.9474 ± 0.0015 | 0.9417 ± 0.0015 | 0.9392 ± 0.0019 | 0.9324 ± 0.0046 |

Decision Tree has the steepest and most consistent degradation across all four targets. LSTM is the flattest across noise levels on G, B, but starts from the lowest baseline on G and A. K-NN and CNN hold up best on C, B, A but K-NN is notably weaker than the others on G at low noise, then overtakes at higher noise.

Accuracy by Fault Combination Multiplicity

No single-line fault examples were present in the test set for any model. SVM was not included in this evaluation.

| Model | Double-line (n) | Double-line Acc | Triple-line (n) | Triple-line Acc | Quadruple-line (n) | Quadruple-line Acc |
| --- | --- | --- | --- | --- | --- | --- |
| CNN | 443 | 0.9910 | 437 | 0.5835 | 211 | 0.9621 |
| Decision Tree | 443 | 0.9729 | 437 | 0.5789 | 211 | 0.8957 |
| K-NN | 443 | 0.9977 | 437 | 0.8215 | 211 | 0.5687 |
| LSTM | 449 | 0.9933 | 544 | 0.4908 | 224 | 0.7679 |

Accuracy by Specific Fault Combination

Only combinations with test examples present are shown. Triple-line faults split sharply by combination: G+B+A stays high across all models, while C+B+A collapses.

| Model | G+A (double) | C+B (double) | G+B+A (triple) | C+B+A (triple) | G+C+B+A (quad) |
| --- | --- | --- | --- | --- | --- |
| CNN | 0.9959 (n=242) | 0.9851 (n=201) | 0.9790 (n=238) | 0.1106 (n=199) | 0.9621 (n=211) |
| Decision Tree | 0.9711 (n=242) | 0.9751 (n=201) | 0.9454 (n=238) | 0.1407 (n=199) | 0.8957 (n=211) |
| K-NN | 0.9959 (n=242) | 1.0000 (n=201) | 0.9748 (n=238) | 0.6382 (n=199) | 0.5687 (n=211) |
| LSTM | 0.9867 (n=225) | 1.0000 (n=224) | 0.9205 (n=264) | 0.0857 (n=280) | 0.7679 (n=224) |

Training Time and Model Complexity

| Model | Training Time (total, s) | Notes |
| --- | --- | --- |
| SVM (RBF) | 8.24 | C=8.0, gamma=scale; support vectors range 401–1828 across targets |
| Decision Tree | 0.17 | max depth 10; leaf count range 18–94 |
| K-NN | 0.09 | K=5, distance-weighted, minkowski p=2; 6288 reference points stored |
| CNN | 161.24 | filters [32, 64], kernel size 2, batch size 32 |
| LSTM | 406.05 | units [64, 32] bidirectional, batch size 16 events, event-sequence input |

Hypothesis Testing (H1–H4)

Evaluated on the 339 rows common to all four models (cnn, dtr, knn, lstm), after dropping rows outside that common set. LSTM had a larger common-set discrepancy (1336 rows dropped) due to its event-based structure.

H1: Fault Detection Accuracy (overall fault occurred, vs relay baseline)

Cochran's Q omnibus across the five methods (four models plus relay): Q = 3.0000, df = 4, p = 0.5578, no significant difference detected.

| Model vs Relay | p-value | Test | Accuracy Diff (pp) | 95% CI | OR |
| --- | --- | --- | --- | --- | --- |
| CNN | 1.0000 | exact | 0.00 | [0.00, 0.00] | n/a |
| Decision Tree | 1.0000 | exact binomial | -0.29 | [-0.87, 0.28] | 0.0000 |
| K-NN | 1.0000 | exact | 0.00 | [0.00, 0.00] | n/a |
| LSTM | 1.0000 | exact binomial | -0.29 | [-0.87, 0.28] | 0.0000 |

No model differs significantly from the relay baseline on overall fault detection.

H2: Per-Line Classification Performance

Cochran's Q omnibus per target, across cnn, dtr, knn, lstm:

| Target | Q | df | p |
| --- | --- | --- | --- |
| G | 8.1333 | 3 | 0.0433 |
| C | 2.2800 | 3 | 0.5164 |
| B | 4.7143 | 3 | 0.1940 |
| A | 9.0000 | 3 | 0.0293 |

G and A show a significant omnibus difference across models; C and B do not. Pairwise McNemar comparisons (deep learning vs classical):

| Target | Comparison | p-value | Test | Diff (pp) |
| --- | --- | --- | --- | --- |
| G | CNN vs DTR | 0.4545 | exact binomial | 1.18 |
| G | LSTM vs DTR | 1.0000 | exact binomial | -0.29 |
| G | CNN vs KNN | 0.2225 | chi2 (cont. corrected) | -2.65 |
| G | LSTM vs KNN | 0.0553 | chi2 (cont. corrected) | -4.13 |
| C | CNN vs DTR | 1.0000 | exact binomial | 0.29 |
| C | LSTM vs DTR | 0.6875 | exact binomial | -0.59 |
| C | CNN vs KNN | 1.0000 | exact binomial | 0.29 |
| C | LSTM vs KNN | 0.6250 | exact binomial | -0.59 |
| B | CNN vs DTR | 0.5000 | exact binomial | 0.59 |
| B | LSTM vs DTR | 0.5000 | exact binomial | 0.59 |
| B | CNN vs KNN | 1.0000 | exact binomial | 0.29 |
| B | LSTM vs KNN | 1.0000 | exact binomial | 0.29 |
| A | CNN vs DTR | 1.0000 | exact | 0.00 |
| A | LSTM vs DTR | 0.2500 | exact binomial | -0.88 |
| A | CNN vs KNN | 1.0000 | exact | 0.00 |
| A | LSTM vs KNN | 0.2500 | exact binomial | -0.88 |

None of the pairwise comparisons reach significance at the 0.05 level, despite the significant omnibus tests for G and A.

H3: Fault Reporting Latency

Wilcoxon signed-rank test on paired per-scenario latency, common 339 rows:

| Comparison | p-value | Hodges-Lehmann Estimate (ms) | 95% CI |
| --- | --- | --- | --- |
| CNN vs DTR | <0.000001 | 0.0849 | [0.0826, 0.0872] |
| LSTM vs DTR | <0.000001 | 343.9481 | [329.0144, 365.2630] |
| CNN vs KNN | <0.000001 | 0.0653 | [0.0629, 0.0677] |
| LSTM vs KNN | <0.000001 | 343.9270 | [328.5322, 364.9509] |

All comparisons are significant. LSTM is markedly slower than both DTR and KNN (roughly 344 ms median difference), while CNN's difference from DTR and KNN is negligible in practical terms despite statistical significance.

H4: Robustness (TOST Equivalence)

Two one-sided tests for equivalence, margin = 5.0 accuracy points. Paired TOST was not computable for LSTM (missing raw trial data).

| Model | Target | 1% vs 5% | 1% vs 10% | 1% vs 20% |
| --- | --- | --- | --- | --- |
| CNN | G | 0.0069, equivalent | 0.0273, equivalent | 0.0784, not equivalent |
| CNN | C | 0.0242, equivalent | 0.0538, not equivalent | 0.1104, not equivalent |
| CNN | B | 0.0242, equivalent | 0.0654, not equivalent | 0.1388, not equivalent |
| CNN | A | 0.0135, equivalent | 0.0474, equivalent | 0.1036, not equivalent |
| Decision Tree | G | 0.0757, not equivalent | 0.1397, not equivalent | 0.2294, not equivalent |
| Decision Tree | C | 0.0910, not equivalent | 0.2003, not equivalent | 0.3338, not equivalent |
| Decision Tree | B | 0.0788, not equivalent | 0.1654, not equivalent | 0.2787, not equivalent |
| Decision Tree | A | 0.0743, not equivalent | 0.1324, not equivalent | 0.2240, not equivalent |
| K-NN | G | -0.0304, equivalent | -0.0350, equivalent | -0.0220, equivalent |
| K-NN | C | 0.0078, equivalent | 0.0214, equivalent | 0.0523, not equivalent |
| K-NN | B | 0.0038, equivalent | 0.0140, equivalent | 0.0401, equivalent |
| K-NN | A | 0.0028, equivalent | 0.0105, equivalent | 0.0327, equivalent |

Values shown are the accuracy difference between noise levels; p_TOST values are omitted here for brevity, all "equivalent" calls hold at p < 0.05 except K-NN B at 1% vs 20% (p = 0.000001). K-NN is the most stable model under noise, holding equivalence at nearly every comparison. Decision Tree fails equivalence at every comparison, consistent with its steep robustness sweep degradation seen earlier. CNN holds equivalence at low noise but breaks down by 20%.